| 1.0 | PURPOSE: |  |  |  |
| --- | --- | --- | --- | --- |
|  | The purpose of this SOP is to lay down the procedure for Sampling Booth. |  |  |  |
| 2.0 | SCOPE: |  |  |  |
|  | ## This procedure is applicable for operation of sampling booth at Innova Pharmactive ## Pvt. Ltd. |  |  |  |
| 3.0 | RESPONSIBILITY: |  |  |  |
|  | 3.1 | Store personnel are responsible for follow this SOP. |  |  |
|  | 3.2 | Incharge (Store) are responsible for the implementation of this Procedure |  |  |
|  | 3.3 | Quality Assurance is responsible for the review, approval, distribution and archival of the SOP. |  |  |
| 4.0 | DEFINITION: NA |  |  |  |
| 5.0 | PROCEDURE: |  |  |  |
|  | 5.1 | Clean the SS top and other parts of Laminar Flow. |  |  |
|  | 5.2 | There shall not be any dust particles in side of the room. |  |  |
|  | 5.3 | Workers and staff members shall be with non particle generating apparel with all accession cap, boot etc. |  |  |
|  | 5.4 | Check electric supply. (Check all III Phase current) |  |  |
|  | 5.5 | Start the laminar flow by pressing the switch. |  |  |
|  | 5.6 | Check the manometer reading (Pressure difference required 10 to 15 MM WG and it shall not exceed above 18 MM WG.) |  |  |
|  | 5.7 | After 10 min of running start the sampling activity |  |  |
|  | 5.8 | MAINTENANCE : |  |  |
|  |  | 5.8.1 | For the efficient working of the laminar flow, maintenance is to be carried out timely as given in annexure -2 (IP/MNT/SOP/001/F2.00). It is necessary to check whether all the parts of the unit are working properly. |  |
|  |  | 5.8.2 | Clean & wash the filter Monthly. Remove the filter element, clean the element and reassemble it. (Maintenance of the filter is depend on the load) |  |
|  |  | 5.8.3 | Check the working of the manometer (oil level) monthly. |  |
|  |  | 5.8.4 | Check and tighten mounting bolts,filter,blower casing and blower motor etc. |  |
|  |  | 5.8.5 | Clean the glass out side as well as inside regularly. |  |
|  |  | 5.8.6 | MAINTENANCE OF THE FILTER: |  |
|  |  |  | 5.8.6.1 | Prefilter-To clean by high pressure air (Depends on use) |
|  |  |  | 5.8.6.2 | 5 micron HEPA Filter to change (Depends on use) |
|  |  |  | 5.8.6.3 | 0.3 micron HEPA filter to replace (Depends on use) |
|  |  |  | Refer the annexure -2 (IP/MNT/SOP/001/F2.00)for maintenance of Sampling Booth |  |
|  |  | 5.8.7 | FAULT CONDITION AND REMEDIES: |  |
|  |  |  | Condition; Cause; Remedies. Low Pressure; Filter Blocked; Clean or replace. Filter Leakage; Replace. Noise in blower; Cheque the blower. |
| 6.0 | ABBREVIATION: |  |  |  |
|  |  | SOP | - Standard Operating Procedure |  |
|  |  | NA | - Not Applicable |  |
|  |  | QAD | - Quality Assurance Department |  |
|  |  | STR | - Store Department |  |
|  |  | WG | - Water gauge |  |
| 7.0 | REFERENCE: Nil |  |  |  |
| 8.0 | ANNEXURE: NA |  |  |  |
| 9.0 | REVISION HISTORY: |  |  |  |
| SOP No.; Revision No.; Effective Date; Change Control No.; Change History. IL/STR/SOP/017; 00; 18/03/2011; CCR/11018; Company Name and Logo Changes. CCR/11021; SOP Procedural Changes. |