| 1.0 | PURPOSE : |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | To lay down the procedure for operation and preventive maintenance of Dispensing Booth. |  |  |  |  |  |  |  |
| 2.0 | SCOPE: |  |  |  |  |  |  |  |
|  | ## This procedure is applicable for operation and preventive Maintenance of Dispensing booth in Organisation. |  |  |  |  |  |  |  |
| 3.0 | RESPONSIBILITY : |  |  |  |  |  |  |  |
|  | 3.1 | Store personnel are responsible for preparation of this SOP. |  |  |  |  |  |  |
|  | 3.2 | Store department personnel are responsible for following the procedure. |  |  |  |  |  |  |
|  | 3.3 | Engineering and maintenance department personnel are responsible for preventive maintenance and repair. |  |  |  |  |  |  |
|  | 3.4 | Store In-charge is responsible for implementation of SOP. |  |  |  |  |  |  |
|  | 3.5 | QAD is Responsible for Review, Approval, Distribution and Maintenance of the SOP. |  |  |  |  |  |  |
| 4.0 | DEFINITION : NA |  |  |  |  |  |  |  |
| 5.0 | PROCEDURE : |  |  |  |  |  |  |  |
|  | 5.1 | Operating procedure for Dispensing Booth : |  |  |  |  |  |  |
|  |  | 5.1.1 |  | Switch on the dispensing booth by pressing power button also switch ‘ON’ the light and blower. |  |  |  |  |
|  |  | 5.1.2 |  | Dispensing booth should be switched “ON” 15 to 20 minutes before starting the activity. |  |  |  |  |
|  |  | 5.1.3 |  | The two pressure gauges are available inside Dispensing booth to indicate the Pressure differential across pre- filter and HEPA filter. |  |  |  |  |
|  |  | 5.1.4 |  | The pressure differential across pre-filter should be 3 mmwc to 8mmwc and across HEPA filter should be 5 mmwc to 20 mmwc. |  |  |  |  |
|  |  | 5.1.5 |  | The pressure differential across pre-filter and HEPA filter will be recorded in pressure differential Recording log as per annexure I of this SOP. |  |  |  |  |
|  |  | 5.1.6 |  | After recording pressure differential across filters, Perform dispensing activity and record its detail in equipment usage log. |  |  |  |  |
|  |  | 5.1.7 5.1.8 |  | Dispense the Raw Material as per current version of SOP for handling and dispensing of Raw Material.(IP/STR/SOP/009). In case of raw material, don’t take dispensing accessories outside of booth, but collect in polybag in booth itself to avoid any contamination outside the booth. And close the raw material bag/drum of dispensed material under dispensing booth unit, before taking it out. |  |  |  |  |
|  |  | 5.1.9 NOTE |  | Put “OFF” the system after use. - Whenever the arrow of monometer found between the numbers scale. Reading should record in a lowest value or round up value of pressure differential monometer. Example: If the value is 10.5 mmwc then note the lowest value i.e. 10.0 mmwc and it can be round up as given in example. - If pressure differential limit i.e. 0.4 to 1.0 mmwc and arrow of magnehelic gauge found between the number scale, then reading should recorded in lowest value of magnehelic gauge. Example: If the value is 0.5 mmwc indicate on magnehelic gauge then note the lowest value i.e. 0.4 mmwc. |  |  |  |  |
|  | 5.2 | Cleaning procedure for Dispensing Booth : |  |  |  |  |  |  |
|  |  | 5.2.1 | Cleaning of the dispensing booth will be considered under the current version of SOP for cleaning and sanitization of Premises (IP/PRD/SOP/044). |  |  |  |  |  |
|  |  | 5.2.2 | Ensure that the blower is “OFF” during cleaning activity. |  |  |  |  |  |
|  |  | 5.2.3 | Clean the Pre-filter protective grills with non-shredding cloth. |  |  |  |  |  |
|  |  | 5.2.4 | Clean the HEPA filter protective with non-shredding cloth. |  |  |  |  |  |
|  |  | 5.2.5 | Clean the tube light and monometer usong non-shredding cloth. |  |  |  |  |  |
|  |  | 5.2.6 | Clean the balance, cable of the balance, switch boards with clean non-shredding cloth. |  |  |  |  |  |
|  |  | 5.2.7 | Clean the side panels of Dispensing booth from inside and outside proceeding from top to bottom using non-shredding cloth. |  |  |  |  |  |
|  |  | 5.2.8 | Cleaning of the Dispensing Booth will not be recorded separately; it will be part of Annexure III of the current version of the SOP for Cleaning and Sanitization of Premises (IP/PRD/SOP/044). |  |  |  |  |  |
|  | 5.3 | Preventive Maintenance procedure for Dispensing Booth : |  |  |  |  |  |  |
|  |  | 5.3.1 The Preventive Maintenance of the Dispensing booth performed on the monthly basis. The following parameters are considered during preventive maintenance. |  |  |  |  |  |  |
|  |  | 5.3.1.1 Pre-filter cleaning : Engineering Designee will dismantle the pre-filter, place it in polybags, and carry it to filter cleaning area for cleaning. 5.3.1.2 After cleaning, it will be properly mounted in its designated location 5.3.1.3 After Cleaning, If reading goes down, it indicates chocking of pre-filter which requires its replacement. 5.3.1.4 If reading goes above after pre-filter cleaning, it indicates chocking of Pre-filter which require its replacement. |  |  |  |  |  |  |
|  |  | 5.3.1.5 Whenever replacement of HEPA filter takes place, the integrity of the filter which should be verified by HEPA filter integrity Test by approved outside agency. 5.3.1.6 Magnehelic Gauge: Engineering Designee will check the end connector, if required tighten the same. |  |  |  |  |  |  |
|  |  | 5.3.1.7 Blower Motor for unusual noise:- Engineering Designee will check any unusual noise of the blower motor |  |  |  |  |  |  |
|  |  | 5.3.1.8 The engineering Designee will check the lubrication of the blower motor bearing and, if necessary, lubricate them |  |  |  |  |  |  |
|  |  | 5.3.1.9 Engineering Designee will check the tightness of mounting bolt, pre-filter, blower chasing and blower motor. 5.3.1.10 Engineering Designee will check the blower light and fluorescent light switches |  |  |  |  |  |  |
| 6.0 | ABBREVIATION : |  |  |  |  |  |  |  |
|  |  | SOP |  |  | : |  | Standard Operating Procedure. |  |
|  |  | NA |  |  | : |  | Not Applicable. |  |
|  |  | QAD |  |  | : |  | Quality Assurance Department. |  |
|  |  | HEPA |  |  | : |  | High Efficiency Particulate Air. |  |
|  |  | mmwc |  |  | : |  | Millimeters per water column. |  |
|  |  | PM |  |  | : |  | Preventive Maintenance. |  |
|  |  | BL |  |  | : |  | Blower Light. |  |
|  |  | FL |  |  | : |  | Fluorescent light. |  |
| 7.0 | REFERENCE : Eudralex Volume 4 Chapter 4: Documentation (Sub Section : Others : 4.31) |  |  |  |  |  |  |  |
| 8.0 | ANNEXURE : |  |  |  |  |  |  |  |
|  | Annexure I |  |  |  |  | : |  | Pressure Differential Recording of Dispensing Booth |
|  |  |  |  |  |  |  |  | (IP/STR/SOP/018/F01.01) |
|  | Annexure II |  |  |  |  | : |  | Preventive maintenance checklist for Dispensing Booth |
|  |  |  |  |  |  |  |  | (IP/STR/SOP/018/F02.02) |
| 9.0 | REVISION HISTORY: |  |  |  |  |  |  |  |
|  | SOP No.; Rev. No.; Effective Date; Change Control No.; Change History. IL/STR/SOP/018; 00; 18/03/2011; -; New. IL/STR/SOP/018; 01; 01/01/2012; CCR/11018; Company Name And Logo changed. CCR/11021; Procedural changes. IP/STR/SOP/018; 02; 25/01/2014; IP/CCR/13/016; Procedural changes. IP/STR/SOP/018; 03; 01/07/2014; IP/CCR/14/026; Editorial changes & New annexure added. IP/STR/SOP/018; 04; 04/052019; IP/CCR/18/068; - Company Logo change. - Procedural changes and Editorial changes. - SOP Format (Header & Footer) change. Changes in Annexure.. IP/STR/SOP/018; 05; 12/03/2020; IP/CCR/20/008; - SOP Title change accordingly change in purpose & scope. - Minor Procedural changes in SOP.. IP/STR/SOP/018; 06; 07/06/2021; IP/CCR/21/032; - Annexure – II arrange in line as per SOP Section 5.2 - Change in SOP Format as per SOP for SOP and Change in Annexure 3. Annexure – II arrange in line as per SOP Section5.2. |
|  | SOP No.; Rev. No.; Effective Date; Change Control No.; Change History. IP/STR/SOP/018; 07; 14/11/2022; IP/CCR/22/065; Incorporate reference of Eudralex volume 4 : Documentation reference and removed checked by sign in Annexure-I. IP/STR/SOP/018; 08; 02/12/2022; IP/CCR/22/079; Incorporate procedural at Section 5 at point no.5.2.5. IP/STR/SOP/018; 09; 16/10/2023; IP/CCR/23/086; - Define the limit of the pressure differential pre-filter and HEPA filter in point no 5.1.4 and updated in Annexure I accordingly.. IP/STR/SOP/018; 10; IP/CCR/24/128; Define the cleaning procedure of dispending booth. |